## Nimruz-TFU Building -
MDM Health Facilities (HF) Program
BoQ_Rehibilation of TFU Project, Ghor Ghori CHC, Khash Rod District-Nimruz Province
| No. | Description of Work | Unit واحد | Quantity مقدار | Cost/Unit (AFN) قیمت فی واحد | Total Cost (AFN) قیمت مجموعی
| 1 | Main Building Civil Works
Mobilization and Demobilization
| 1.1.1 | Mobilization - Compensation in full for the cost for establishing the camp transport of equipment, materials and personnel on the project site | LS | 1
| 1.1.2 | Demobilization - Compensation in full for the cost of removing and cleaning of the camp and construction site, equipment, facilities and personnel from the site and Post construction works, clean up and hand over, along with any details may require to the full satisfaction of Consultancy inspection Engineer | LS | 1
Sub Total for 1.1
| 1.2 | Plain and Reinforced Concrete
| 1.2.2 | PCC M150 with (100) mm thick, for roof according to the drawing and technical specification(See drawings), All task for this item to be under full approval and satisfaction of Engineer | m3 | 45.21
Sub Total 1.2
| 1.3 | Cement Plaster
| 1.3.1 | Interior Plastering 20mm thick,1:3 cement sand smooth plaster to all interior walls, All task for this item to be under full approval and satisfaction of Engineer. | m2 | 150
| 1.3.2 | Exterior Plastering 20 mm thick ,1:3 cement sand smooth plaster to all exterior brick masonry walls, parapet walls, cantilever and louver, and escape stair. All task for this item to be under full approval and satisfaction of Engineer. | m2 | 50
| 1.3.3 | Removing the existing plaster and 'Replaster of Ceiling 20mm thick, 1:3 cement sand smooth plaster to all ceiling surface and stairs, All task for this item to be under full approval and satisfaction of Engineer. | m2 | 490
Sub Total 1.3
| 1.4 | Painting
| 1.4.1 | Interior Painting of TFU Building, Three coats of 75% best quality plastic paint (washable), Brand:(Jotun or Equivalent) to interior walls by applying primer, filling in etc complete in color as directed by the supervisor. All task for this item to be under full approval and satisfaction of Engineer | m2 | 880
| 1.4.2 | Exterior Painting of TFU Building, Three coats of approved weather shield paint(100%) Brand:(Jotun or Equivalent) to exterior walls including all surfaces preparation by applying wall sealer primer complete in color as directed by the supervisor. All task for this item to be under full approval and satisfaction of Engineer | m2 | 317
| 1.4.3 | Painting of (Ceiling) Three coats of matt water based (acrylic) white color paint Brand:(Jotun or Equivalent) to all specified ceiling surfaces including all preparation, primer, filling in etc. to all ceiling surface and stairs, All task for this item to be under full approval and satisfaction of Engineer | m2 | 405
Sub Total 1.4
| 1.5 | Doors and Windows
| 1.5.1 | This item cover Doors D1….Dn, on best quality Turkish origin or equivalent UPVC (7000) door 2mm thick in white color includes supplying, installation, hardware (Hinge, Lock, Door Stopper, Door Closer, and all other accessories), double glass 4mm each and 12mm gap between two glass, anti- blast film on inner glazing layer, and any other accessories and auxiliary materials including joint sealer (if required) etc. All door shall be according to Door Schedules, Drawings, Technical Specifications, and in charge Engineer approval. Product brand will be approved by Engineer. Reference Drawing: | m2 | 65
| 1.5.2 | This item cover Doors D1….Dn, with major repairing, includes supplying, installation, hardware (Hinge, Lock, Door Stopper, Door Closer, and all other accessories), double glass 4mm each and 12mm gap between two glass, anti- blast film on inner glazing layer, and any other accessories and auxiliary materials including joint sealer (if required) etc. All door shall be according to Door Schedules, Drawings, Technical Specifications, and in charge Engineer approval. Product brand will be approved by Engineer. Reference Drawing: | LS | 1
| 1.5.3 | This item cover Doors D1….Dn, with minor repairing, includes supplying, installation, hardware (Hinge, Lock, Door Stopper, Door Closer, and all other accessories), double glass 4mm each and 12mm gap between two glass, anti- blast film on inner glazing layer, and any other accessories and auxiliary materials including joint sealer (if required) etc. All door shall be according to Door Schedules, Drawings, Technical Specifications, and in charge Engineer approval. Product brand will be approved by Engineer. Reference Drawing: | LS | 1
| 1.5.4 | This item cover windows W1….Wn, on best quality Turkish origin or equivalent UPVC (7000) frames 2mm thick in white color includes supplying, installation, hardware (Hinge, Lock, fly screen), double glass 4mm each and 12mm gap between two glass, anti- blast film on inner glazing layer, and any other accessories and auxiliary materials including joint sealer (if required) etc. All windows shall be according to windows Schedules, Drawings, Technical Specifications, and in charge Engineer approval. Reference Drawing: Architecture Drawings Note: This item includes grill for safety and security purpose, grill should be totally as per engineer full satisfaction and approval. | m2 | 25
| 1.5.5 | This item cover windows W1….Wn,whit major repair, includes supplying, installation, hardware (Hinge, Lock, fly screen), double glass 4mm each and 12mm gap between two glass, anti- blast film on inner glazing layer, and any other accessories and auxiliary materials including joint sealer (if required) etc. All windows shall be according to windows Schedules, Drawings, Technical Specifications, and in charge Engineer approval. Reference Drawing: Architecture Note: This item includes grill for safety and security purpose, grill should be totally as per engineer full satisfaction and approval. | LS | 1
| 1.5.6 | This item cover windows W1….Wn, with minor repairing, includes supplying, installation, hardware (Hinge, Lock, fly screen), double glass 4mm each and 12mm gap between two glass, anti- blast film on inner glazing layer, and any other accessories and auxiliary materials including joint sealer (if required) etc. All windows shall be according to windows Schedules, Drawings, Technical Specifications, and in charge Engineer approval. Reference Drawing: Note: This item includes grill for safety and security purpose, grill should be totally as per engineer full satisfaction and approval. | LS | 1
Sub Total 1.5
| 1.6 | Tiling Works
Granite Tilling Works
| 1.6.1 | Granite Skirting black colour by size (600x150x15) mm set into 1:2 cement sand mortar base on all interior rooms and corridors, All task for this item to be under full approval and satisfaction of Engineer | m | 20
Mosaic work for roof and rump
| 1.6.2 | Mosaic work for roof set into 1:2 cement sand mortar, All task for this item to be under full approval and satisfaction of Engineer, Reference Drawing: | m2 | 475
PVC Vinyl Works
Ceramic Tiling Works
| 1.6.4 | Floor Ceramic tiles: Supply and installation of anti-slip ceramic tiles by size (300x300x8)mm white colour set into 1:2 cement sand mortar base on Toilets, Kitchen floor, and Sterilization Room surfaces, best quality brand to be original Iranian or equivalent, All task for this item to be under full approval and satisfaction of Engineer | m2 | 40
Sub Total 1.6
| 1.7 | Tinsmith Works
| 1.7.1 | GI Iron size (120x150)mm , 3.5 m Length Gauge ( 22 ) (downspout), for roof rain water, All task for this item to be under full approval and satisfaction of Engineer the cost includes complete package of roof drain, clamps, stainers, straps, insulation materials needed, painting, and all related materials, works and accessories. All work to be done as per drawings, specs, and in charge Engineer satisfaction | m | 28
Sub Total 1.7
| 1.8 | Other Works
| 1.8.1 | Kitchen Table & Cabinet : 1- Supply and Preparation of Wooden Table size (600mm Depth, 900mm Height and 5800mm Length) from best quality of Turkish lassani board (T=16mm), light colour. Including Granite stone (thickness: 30mm) iranian best quality or equivalent on top of the cabinet complete with all required activities, accessories, related works. Should be under full approval and satisfaction of Engineer. 2- The wooden cabinet above table size (40mm Depth, 600mm Height and 3800mm Length) including hardware (Hinge, Lock, and all other activities, related work, related materials, and all other activities), Turkish quality, complete with all required activities and materials, All task for this item to be under full approval and satisfaction of Engineer. This Item includes supply and installation of stove as per drawings, Specs, and in charge engineer satisfaction. All works should be done as per drawings, specs and satisfaction of Engineer. | Job | 1
| 1.8.2 | Sterilization Room Table & Cabinet : 1- Supply and Preparation of Wooden Table size (600mm Depth, 900mm Height and 5800mm Length) from best quality of Turkish lassani board (T=16mm), light colour. Including Granite stone (thickness: 30mm) iranian best quality or equivalent on top of the cabinet complete with all required activities, accessories, related works. Should be under full approval and satisfaction of Engineer. 2- The wooden cabinet above table size (40mm Depth, 600mm Height and 5800mm Length) including hardware (Hinge, Lock, and all other activities, related work, related materials, and all other activities), Turkish quality, complete with all required activities and materials, All task for this item to be under full approval and satisfaction of Engineer. All works should be done as per drawings, specs and satisfaction of Engineer. | Job | 1
|  | Supply in installation of Isogam for roof with all required activities | m2 | 490
|  | supply brick pice work for roof slope as per drawing. | m3 | 45
Sub Total for 1.8
| 1.9 | Ladder
| 1.9.1 | Ladder: This item covers complete ladder set for access to the roof including: 1- Supply and installation of 5mm thick steel base plate for connecting of steel ladder to the concrete pad. Including all the accessories, fixings and workmanship as per specifications, engineer approval and drawings. 2- Supply and installation of anchor bolt Dia 12mm, length=100mm for steel ladder including all the accessories, fixings and workmanship as per specifications, engineer approval and drawings. 3- Steel pipe: Supply and Installation of steel pipe Dia=40, thickness=3mm for steel ladders including all the accessories, fixings and workmanship as per specifications, engineer approval and drawings. 4- Painting of all non-galvanized surfaces, which consists of one coat of anti-rust followed by two coats of oil-based painting. 5- All other accessories, fixings and workmanship as per specifications, engineer approval and drawings. | Set | 1
Sub Total for 1.9
| 2 | Water & Sewer Plumbing System
| 2.1 | Inside Water & Sewer Plumbing System
| 2.1.1 | Supply & Installation of Type PN10 PPRC pipe best quality (Turkish brand) of accepted standards or equivalent with all necessary specials laid in water distribution system buried in brick walls / floor or clipped to any location where necessary. Complete in all respect and as per drawings, specifications & in-charge Engineer approval. All pipes and fittings should be in accordance to drawings and specification, for more detail See Plumbing drawings. | LS | 1
| 2.1.10 | Hand Wash Basin: Supply & installation of white hand wash basin (Ceramic) of size as per drawing with 15mm cp pillar tap 15mm, CP angular cock, 15mm, PVC connector with both ends coupling, 32mm CP bottle trap 32mm CP waste coupling with plug, with single hole mixture by master / sonex( or approved equal.), (Imported) Porta or Equal all complete and all other relatives accessories and materials, complete in all respect and as per drawings & specifications & in-charge Engineer approval. For more detail & information see Plumbing drawings, details & Technical Specification. The rate should be include all materials, process, workmanship, wages & transportations, tests required for checking of complete piping system. | Note
| 2.1.11 | supply & installation of Hand Wash Basin Complete Set. (See the Plumbing and Architectural drawings). | set | 11
| 2.1.12 | kitchen Sink: (size as per drawing) by Reginox with Mixer by Master/Sonex , pop-up waste set , two Stop Cocks for cold & hot water (angle cock Valves) by aster/Sonex,soap dish/glass shelf, Bottle trap all complete, and all other relatives accessories and materials, complete in all respect and as per drawings & specifications & in-charge Engineer approval. For more detail & information see Plumbing drawings ,details & Technical Specification. The rate should be include all materials, process, workmanship,wages & transportations,tests required for checking of complete piping system. | Note
| 2.1.13 | supply & installation of 2 * 600x600mm Kitchen Sink Stainless Steel, Complete Set, equivalent and approved by in-charge Engineer.,(See the Plumbing drawings. | Set | 2
| 2.1.14 | Miror Set : standard and approved quality Towel rail, Mirror & Soap dispenser shelf all complete, and all other relatives accessories and materials, equivalent standard and approved by in-charge Engineer. For more detail & information see Plumbing drawings & details. Complete in all respect and as per drawings & specifications & in-charge Engineer approval. For more detail & information (See Plumbing drawings. | Note
| 2.1.15 | Supply and installation of Stainless Steel Towel rail complete.(See Plumbing drawings) | Set | 11
| 2.1.16 | Supply & installation of complete high quality Mirror, 600x400x5mm, set with all necessary item & materials.(See Plumbing drawings) | Set | 11
| 2.1.17 | Supply & installation of complete Stainless Steel Soap dispenser. set with all necessary item & materials.(See Plumbing drawings ) | Set | 11
| 2.1.18 | Water tank: Supply & installation of 2000 Liter Galvanized Steel Water tank including insulation (HIGH DENSE GLASS WOOL) and external sheet, ladder with all necessary items base plate, stands, strap to fasten the tank with the stand, accessories as per drawings & specification and approved by in charge Engineer,(See Architectural & Civil drawings ). | Set | 1
| 2.1.21 | Electrical water Heater: Supply & installation of Electrical water Heater Ariston brand or equivalent, with 50 Liter Capacity 220V-1ph-50HZ with all necessary fittings and valves.as per drawings & specification and approved by in charge Engineer, (See Plumbing drawings Sheet# P01-P02-P03). | Set | 3
Sub Total for 2.1
| 2.2. | Outside Water, Sewer and drainage Systems
| 2.2.1 | Domestic Water Pipe: Supply & Installation of Type PN16 PPRC pipe and fittings for site and well pump with all necessary specials laid in water distribution system buried underground, in brick walls / floor or clipped to any location where necessary. | Note
| 2.2.2 | Supply and installation of type PN16 PPRC pipe 1-inch | m | 80
| 2.2.3 | Gate Valves: Supply & installation of Gate Valves & Check Valve PN 16approved Quality including all accessories and material as specified all complete. | Note
| 2.2.4 | Gate Valve,25mm (1") diameter.(See the Civil drawings). | Each | 1
Sub Total of 2.2
| 3 | Electrical System
| 3.1 | Power & Lighting System
| 3.1.1 | Supply and installation of 10A, 230V, Recessed mounted, single pole lighting switchs. According to drawing with all required activity and accessories | No | 53
| 3.1.2 | Supply and installation of 12A, 230V, Recessed mounted waterproof two pin sockets. According to drawing with all required activity and accessories | No | 43
| 3.1.3 | Supply and installation of 1Cx2.5mm2 PVC insulated copper cable for lighting made in turkey, with all required activities and accessories. | m | 450
| 3.1.4 | Supply and installation of 1Cx4mm2 PVC insulated copper cable for power sockets made in turkey, with all required activities and accessories. | m | 1320
| 3.1.5 | Supply and installation of outlet box circular Metallic with all required activities. | Each | 114
| 3.1.6 | Supply and installation of junction box large size metallic with all required activities. | Each | 48
| 3.1.7 | Supply and installation of fan switch with all required activities. | Each | 18
| 3.1.8 | Supply and installation of Wire (solid) 1(1C_2.5mm2) for Grounding based on the design and specification with all required activities. | m | 310
| 3.1.9 | Supply and installation of condescend, lamps (24W) with all required activities. | Each | 8
| 3.1.10 | Supply and installation of Neon Lamps (pair), (40 W) with all required activities. | Set | 2
| 3.1.11 | Supply and installation of Neon Lamps (single), (80 W) with all required activities. | Set | 10
|  | Supply and installation of Lamps (single), (24 W) with all required activities. | Set | 37
| 3.1.13 | Supply and installation of Panel board (PB-TFU2, per drawing), 50 AT. according to drawing with all required activities and accessories | No | 1
| 3.1.15 | Supply and installation of PVC4'' such 40 conduits with one spare conduit from Changeover to MDP according to drawing with all required activities and accessories | m | 15
| 3.1.16 | Supply and installation of 4x16mm2 + 16mm2 Cu, XLPE/PVC insulated cable, from PB-TFU to MDP-TFU in 2" conduit. | m | 14
| 3.1.17 | Supply and installation of grounding system consisted of four 20x3000mm copper clad steel ground rods and 95mm2 bare copper conductor. according to drawing with all required activities and accessories | No | 1
| 3.1.18 | Supply and installation of 1x25mm2 PVC insulated grounding copper cable made in turkey, with all required activities and accessories. | m | 15
Total for 3.1
| 3.2 | BoQ for Electricity Solar Panel System (18)kw with (40) kw Backup
| 3.2.1 | Supply and installation high quality, Monocrystalline Solar Panel Half cut double glass Grade A, 600Wp, 46.82V DA SOLAR or equivalent it should be test and confirmed by a standard laboratory completing of work with all its included details. | No | 36
| 3.2.2 | Supply and installation of high-quality,3phase Growatt hybrid inverter, 6kw,48VDC or its equivalent, completing of work with all its included details. | No | 3
| 3.2.3 | Supply and installation of high quality, lithium battery Pack 306AH, 10kw, Voltage 51.2v, Cycle life:6000 cycle, SGE Brand or equivalent, completing of works with all its included details. | No | 4
| 3.2.4 | supply and Installation of high quality steel box 100x100x3mm structure for mounting of SOLAR PANELS. Quantities to be arrived at considering 22, 600Wp ,PV panel for one inverter as per drawing details / structure, completing of works with all its included details. | No | 2
| 3.2.5 | Supply and installation of high quality Combiner box 100A in-put and output breakers for four inverters with all accessories for outdoor usage with weather proof enclosure. Each junction boxes shall be provided with suitable metal oxide varistors ( Mov's) / surge arresters, | No | 1
| 3.2.6 | Supply and installation of high-quality DC Distribution panel board including DC breakers and as per the drawing one panel will feed two inverters and should have necessary surge arresters, completing the works with all its included details. | No | 1
| 3.2.7 | Supply and installation of(1x6 mm2) single strand Annealed high conductivity copper conductor, FRLS PVC insulated 1100 V rating flexible wires for D.C side in PVC conduit. And each solar panel should be grounding. | m | 200
| 3.2.8 | Supply and installation of high quality,(4x35+G16 mm2) Multi strand copper Cable ,completing of works with all its included details. | m | 15
| 3.2.9 | Supply and installation of high quality 100 AMP 3phase,Manual Changeover ,completing of works with all its included details. | No | 1
| 3.2.10 | Supply and installation of high quality 20A/1000V,DC CIRCUIT BREAKER and DC SPD ,completing of works with all its included details. | No | 4
| 3.2.11 | Supply and installation of high quality 250 AMP,DC CIRCUIT BREAKER ,completing of works with all its included details. | No | 2
| 3.2.12 | Supply and installation of high quality 32 AMP,DC ISOLATROR ,completing of works with all its included details. | No | 4
| 3.2.13 | Supply and installation of high quality 63 AMP,AC ISOLATROR and AC SPD ,completing of works with all its included details. | No | 2
| 3.2.14 | Supply and installation of high quality 32 AMP,3 phase AC CIRCUIT BREAKER ,completing of works with all its included details. | No | 2
| 3.2.15 | Supply and installation of high quality (20cm )1x25mm2 battery cables with all accessories (cable,clamp,lugs and end termination), completing of works with all its included details. | No | 2
Total for 3.2
| 4 | Mechanical System (Ref. Spec. 7.1 Mechanical Services)
| 4.1.1 | Air condition system: Supply and installation of approved type Air condition system Cooling & Heat Pump type 18000 BTUH - 220 V-1ph-50HZ , brand: Samsung/Daikin/Carrier, complete with all necessary accessories to make it functional, For more detail & information (See Mechanical drawings Sheet# M01-M02-M03). | Set | 2
| 4.1.2 | Air condition system: Supply and installation of approved type Air condition system Cooling & Heat Pump type 12000 BTUH - 220 V-1ph-50HZ , brand: Samsung/Daikin/Carrier, complete with all necessary accessories to make it functional, For more detail & information (See Mechanical drawings Sheet# M01-M02-M03). | Set | 1
| 4.1.3 | Wall/Window Mounted Exhaust Fan (EX-03): Supply and installation of approved type Wall mounted Exhaust Fan Air Flow = 200 CMH - 1phase-220Volt-50HZ- Input power=28watt (ELICENT or equivalent) complete with all necessary accessories to make it functional, For more detail & information (See Mechanical drawings Sheet# M01-M02-M03). | Set | 6
| 4.1.4 | 100mm PVC Ductwork: Supply and installation of approved type 100mm PVC ductwork with all necessary accessories to make it functional, For more detail & information (See Mechanical ) | m | 3
| 4.1.5 | Fire Extinguisher: Supply and installation of approved Multi-Purpose Powder Fire (ABCE) 20 lb - Fire Extinguisher (Made in USA or equivalent)For more reference see Mechanical Drawing sheets M-01,M-02,M-04.& specification. | Set | 2
| 4.1.6 | Multi-Purpose Gas (CO2) 13 lb - Fire Extinguisher: Supply and installation of approved Multi-Purpose Gas (CO2) 13 lb - Fire Extinguisher (Made in USA or equivalent)For more reference see Mechanical Drawing sheet M-01,M-02,M-04 & specification page 267. | Set | 2
| 4.1.7 | Ceiling Fan: Supply and installation of 48" aluminium alloy ceiling fan, 330 RPM, 250 CMM, 80 Watts, 3 blades, GFC brand or equivalent, with controller and all associated work as per drawings, specifications, and engineer approval | No | 21
| Sub Total of 4.00 | 4.1
GRAND TOTAL FOR TFU building