## DATA (hidden)
ID#: | A211655
Province: | Badghis
District : | QIN
Village : | Arbab Mohammad
Project Purpose: Construction of Solar Powered Water Supply Network
USD Rate | 0 | 0
Item | Quantity | Unit | Total
Cement | 1 | ton | 0
Reinforcing Bar | 1 | ton | 0
Tap Stand No | 8
L pipe
Total Length of Pipe | 1771
Targeted papulation 150 Family, 1050 People
150

## DATA1 (hidden)
ID#: | BHA-DP.2025
Province: | Badghis
District : | Qala-e-eNaw
Village : | Taymani Darah
Project Purpose: | Repiaring of Garvity water supply Network
Tap Stand No | 34
Summary | Repiaring main and distribution pipes, reservoir and Public STPs
Targeted papulation Family
473 | Family
3311 | Population

## QUT, Estimation (hidden)
Project: | IOM-WASH |  |  | Province: | Badghis |  | Date: | 2026-07-16
ID#: | BHA-PD.2025 |  |  | District : | Qala-e-eNaw
Repiaring of Garvity water supply Network |  |  |  | Village : | Taymani Darah
S/N | Particulars of Items شرح موضوع | No. تعداد | Area مساحت |  | Length طول | tickness/length صخامت /طول | Qty مقدار | Total Qty مقدارمجموعی | Unit مقدار
1 | Site prepration | [6 empty] | 621.4 | M2
1.01 | Site prepration Reservoir | 1 | b*h | 5 | 5 | 1 | 25 | 25 | M2
1.02 | Site prepration for tap stand | 34 | b*h | 2.8 | 2 | 1 | 5.6 | 190.4 | M2
1.03 | Site prepration for pressure breaker,Valve box's and spring chamber | 6 | b*h | 1 | 1 | 1 | 1 | 6 | M2
1.04 | Site prepration and cleaning for speing area and spring chamber | 1 | b*h | 20 | 20 | 2 | 400 | 400 | M2
2 | Excavation | [6 empty] | 329.224 | M3 | 0.26
2.01 | Excavation for mine pipe scheme | 290 | b*h*L | 0.4 | 0.8 | 1 | 0.32 | 92.8 | M3
2.02 | Excavation around Stone masonary water reservoir for outside plastaring and pointing | 1 | b*L*d | 0.5 | 1.5 | 20 | 15 | 15 | M3
2.03 | Excavation for tap stand | 34 | b*t | 0.456 |  |  | 0.456 | 15.504 | M3
2.04 | Excavation for river crossing | 115 | b*h*L | 0.4 | 1 | 2 | 0.8 | 92 | M3
2.05 | Excavation for mine distribution pipe | 33 | b*h*L | 0.4 | 0.8 | 1 | 0.32 | 10.56 | M3
2.06 | Excavation for STP sock pit | 34 | b*h*L | 2.0096 |  |  | 0.8 | 27.2 | M3
2.07 | Excavation for STP pipes | 238 | b*h*L | 0.4 | 0.8 | 1 | 0.32 | 76.16 | M3
2.08 | Excavation for Valve Box | 1 | b*h*L | 1 | 1 | 0.5 | 0.5 | 0.5 | m3
3 | PCC 150 (1:2:4) | [6 empty] | 21.5676 | M3
3.01 | PCC for top slab of reservoir | 1 | b*L*h | 5 | 5 | 0.05 | 1.25 | 1.25 | M3
3.02 | PCC of tap stand | 34 | b*h*L | 0.0564 |  |  | 0.0564 | 1.9176 | M3
3.03 | PCC for river crossing | 115 | b*h*t | 0.4 | 0.4 | 1 | 0.16 | 18.4 | M3
4 | RCC 250 (1:1:2) |  | b*h |  |  |  |  | 11.1628 | M3
4.01 | RCC of STP 1 | 34 | L*b*h | 0.3 | 0.3 | 0.73 | 0.0657 | 2.2338 | M3
4.02 | RCC of STP 2 | 34 | L*b*h | 1.2 | 1.1 | 0.1 | 0.132 | 4.488 | M3
4.03 | RCC of STP 3 | 34 | L*b*h | 0.1 | 0.2 | 5 | 0.1 | 3.4 | M3
4.04 | RCC of Pressuer breaker box's slab | 5 | L*b*h | 1 | 1 | 0.1 | 0.1 | 0.5 | M3
4.05 | RCC of reservoir Valve box's walls | 1 | L*b*h | 3.6 | 1 | 0.1 | 0.36 | 0.36 | M3
4.06 | RCC of reservoir Valve box's top slab | 1 | L*b*h | 0.9 | 0.9 | 0.1 | 0.081 | 0.081 | M3
4.07 | RCC of reservoir Valve box's bottom slab | 1 | L*b*h | 1 | 1 | 0.1 | 0.1 | 0.1 | M3
5 | Pointing - M300 | [6 empty] | 30
5.01 | Poinging Work of out side of reservoir | 1 | b*h | 20 | 1.5 | - | 30 | 30 | M2
6 | Painting | [6 empty] | 111.384
6.01 | Painting for STPs 1 | 34 | b*h | 1.2 | 0.73 | 1 | 0.876 | 29.784 | M2
6.02 | Painting for STPs 2 | 34 | b*h | 1.3 | 1.2 | 1 | 1.56 | 53.04 | M2
6.03 | Painting for STPs 3 | 34 | b*h | 0.56 | 1.5 | 1 | 0.84 | 28.56 | M2
7 | Shuttering | [6 empty] | 21.544
7.01 | Shuttering for tap stand bed | 34 | b*h | 1.56 |  | 0.2 | 0.312 | 10.608 | M2
7.02 | Shuttering for tap stand | 34 | b*h | 0.3 | 4 | 0.68 | 0.204 | 6.936 | M2
7.03 | Shuttering for valve box | 1 | b*h | 4 | 1 | 1 | 4 | 4 | M2
8 | Plaster with Water Proof Powder | [6 empty] | 46.4
8.01 | Waterproof Powder Plaster for wall of Water reservoir | 4 | P*h | 2.4 | 4 | 1 | 9.6 | 38.4 | M2
8.02 | Waterproof Powder Plaster for floor of the Spring chamber in side | 1 | b*h | 4 | 2 | 1 | 8 | 8 | M2
9 | Plaster with cement | [6 empty] | 131.944
9.01 | Plaster for STPs bed and slab | 34 | P*h | 1.5 | 1.4 | 1 | 2.1 | 71.4 | M2
9.02 | Plaster for STPs Stand | 34 | P*h | 1.2 |  | 0.73 | 0.876 | 29.784 | M2
9.03 | Plaster for STPs Drinage | 34 | P*h | 0.56 | 1.5 | 1 | 0.84 | 28.56 | M2
9.04 | Plaster for Spring cahment | 1 | P*h | 2.2 | 1 | 1 | 2.2 | 2.2 | M2
10 | Reinforcement | dia | L*kg/L | L (m) | kg/L | 1 | kg | 630.4164
10.01 | Reinforcement for preesure breaker and spring chember slab | 12 | L*kg/L | 20 | 0.888 | 6 | 17.76 | 111.888 | KG
10.02 | Reinforcement for STPs | 10 | L*kg/L | 4.64 | 0.61667 | 34 | 2.8613 | 102.1496 | KG
10.03 | Reinforcement for STPs | 8 | L*kg/L | 25.6 | 0.39467 | 34 | 10.1035 | 360.6938 | KG
10.04 | Reinforcement for valve box | 10 | L*kg/L | 86 | 0.61667 | 1 | 53.0333 | 55.685 | KG
11 | Earthwork (Backfilling with soil and compaction) | [6 empty] | 313.98
11.01 | Backfilling for mine pipe scheme | 290 | L*b*h | 0.4 | 0.8 | 1 | 0.32 | 92.8 | M3
11.02 | Backfilling around of water reservoir | 1 | b*h*L | 0.5 | 1.5 | 20 | 15 | 15 | M3
11.03 | Backfilling of river crossing | 115 | b*h*L | 1.6 | 0.4 | 1 | 0.64 | 73.6 | M3
11.04 | Backfilling for mine distribution pipe | 33 | b*h*L | 0.3 | 4.6 | 1 | 1.38 | 45.54 | M3
11.05 | Backfilling for STP sock pit | 34 | b*h*L | 0.4 | 0.8 | 1 | 0.32 | 10.88 | M3
11.06 | Backfilling for STP pipes | 238 | b*h*L | 0.4 | 0.8 | 1 | 0.32 | 76.16 | M3
12 | Graveling | [6 empty] | 57.3811
12.01 | Graveling around the Tap Stand and sock pit | 34 | b*L*t | 1.6877 |  |  | 1 | 57.3811 | M3
13 | Stone Pitching around the Spring | [6 empty] | 80
13.01 | Stone pitching from rivrt stone for prevention of water contimenation | 1 | b*h*L | 20 | 20 | 0.2 | 80 | 80 | M3

## Distriution Network Detail BOQ (hidden)
Project: | IOM-WASH |  |  | Province: | Badghis
ID#: | BHA-DP.2025 |  |  | District : | Qala-e-eNaw
Date: | 2026-07-16 |  |  | Village : | Taymani Darah
[6 empty] | Total cost |  | 14326.29 | 213.8252
Bold items to be filled in by tenderer (A1,A2,F... Etc.). Light items are for cost estimation purposes only (by CDC)
Title | No. | Norm/unit | A* | Supplier | Item | Quantity | Unit | Unit cost | Total cost
|  |  | Norm |  |  |  |  | Afs | Afs
A | Water Distribution Scheme
A1 | 1 |  |  |  | Site preparation fo STPs and Reservoir | 621.4 | m2 | 20 | 12428
| 1.01 | 0.04 |  | Local | Site preparation, clearing site etc. | 24.856 | md | 500 | 12428
A2 | 2 |  |  |  | Excavation | 329.224 | m3 | 405 | 133335.72
| 2.01 | 0.9 |  | Local | Unskilled labor | 296.3016 | md | 450 | 133335.72
A3 | 3 |  |  |  | PCC M150 (1:2:4) | 21.5676 | m3 | 6234.9 | 134471.8292
| 3.01 | 1.157 |  |  | Sand & gravel | 24.9537 | m3 | 700 | 17467.5992
| 3.02 | 350 |  |  | Cement | 7548.66 | kg | 9 | 67937.94
| 3.03 | 150 |  |  | water | 3235.14 | liter | 0 | 0
| 3.04 | 0.65 |  |  | Skilled labour on site | 14.0189 | md | 1000 | 14018.94
| 3.05 | 3.25 |  |  | Unskilled labour on site | 70.0947 | md | 500 | 35047.35
Mixer and vibrator should be used for concrete placing, posibally washed crushed agregate is used, water is drikable water, fresh portland or Charat cement is used, at least 15 days curing
A4 | 4 |  |  |  | Pointing ( M:400, 1:3 ) | 30 | m2 | 229.8 | 6894
| 4.01 | 0.024 |  |  | Sand | 0.72 | m3 | 700 | 504
| 4.02 | 2 |  |  | Cement | 60 | kg | 9 | 540
| 4.03 | 1 |  |  | Water | 30 | liter | 0 | 0
| 4.04 | 0.17 |  |  | Skilled labour on site | 5.1 | md | 1000 | 5100
| 4.05 | 0.05 |  |  | Unskilled labour | 1.5 | md | 500 | 750
A5 | 5 |  |  |  | RCC M:250 (1:1:2) | 11.1628 | m3 | 6843 | 76387.0404
| 5.01 | 1.01 |  |  | Sand and Gravel | 11.2744 | m3 | 700 | 7892.0996
| 5.02 | 400 |  |  | Cement | 4509.7712 | kg | 9 | 40587.9408
| 5.03 | 150 |  |  | water | 1691.1642 | liter | 0 | 0
| 5.04 | 0.7 |  |  | Skilled labour on site | 7.814 | md | 1000 | 7813.96 | 15056.2835
| 5.05 | 3.6 |  |  | Unskilled labour on site | 40.1861 | md | 500 | 20093.04
Stone should be crushed mountain stone, sand and water is clean, cement should not be more than 3 months old, the cement - sand proportion will be considered
A6 | 6 |  |  |  | Reinforcement | 630.4164 | kg | 121.34 | 76494.7211
| 6.01 |  |  |  | Steel bar 8 mm | 360.6938 | Kg | 110 | 39676.3136
| 6.02 |  |  |  | Steel bar 10mm | 157.8346 | Kg | 110 | 17361.806
| 6.03 |  |  |  | Steel bar 12 mm | 111.888 | Kg | 110 | 12307.68
| 6.04 | 0.007 |  |  | wire 1 mm | 4.4129 | Kg | 120 | 529.5497
| 6.05 | 0.007 |  |  | Skilled labour on site | 4.4129 | md | 1000 | 4412.9145
| 6.06 | 0.007 |  |  | Unskilled labour on site | 4.4129 | md | 500 | 2206.4573
6.07
A7 | 7 |  |  |  | Shuttering | 21.544 | m2 | 705 | 15188.52
| 7.01 | 0.02 |  |  | Wooden timber | 0.43088 | m3 | 20000 | 8617.6
| 7.02 | 2 |  |  | Wooden pole 3 m long | 43.088 | pcs | 0 | 0
| 7.03 | 0.05 |  |  | Nail | 1.0772 | kg | 100 | 107.72
| 7.04 | 0.2 |  |  | Skilled labour on site | 4.3088 | md | 1000 | 4308.8
| 7.05 | 0.2 |  |  | Unskilled labour on site | 4.3088 | md | 500 | 2154.4
Before placing concrete shuttering is checked that it is well tied and no space between two planks
A8 | 8 |  |  |  | BackFilling | 313.98 | m3 | 67.5 | 21193.65
| 8.01 | 1 |  |  | Soil | 313.98 | m3 | 0 | 0
| 8.02 | 0.15 |  |  | Unskilled labour on site | 47.097 | md | 450 | 21193.65
Soil filling should be well compacted
A9 | 9 |  |  |  | Graveling | 57.3811 | m3 | 850 | 48773.952
| 9.01 | 1 |  |  | River Gravel | 57.3811 | m3 | 600 | 34428.672
| 9.02 | 0.5 |  |  | Unskilled labour on site | 28.6906 | m3 | 500 | 14345.28
Soil filling should be well compacted
A10 | 10 |  |  |  | Painting | 111.384 | m2 | 250 | 27846
| 10.01 | 1 |  |  | Painting the the STPs according to site engineer requerment | 111.384 | m2 | 250 | 27846
A11 | 11 |  |  |  | Water Proof Plaster | 46.4 | m2 | 350 | 16240
| 11.01 | 1 |  |  | Water proof plaster | 46.4 | m2 | 350 | 16240
A12 | 12 |  |  |  | Plaster with cement (1:5) all areas according to drawing | 131.944 | m2 | 231.1 | 30492.2584
| 12.01 | 0.011 |  |  | Sand | 1.4514 | m3 | 700 | 1015.9688
| 12.02 | 2.6 |  |  | Cement (1:5) | 343.0544 | kg | 9 | 3087.4896
| 12.03 | 2.3 |  |  | water | 303.4712 | liter | 0 | 0
| 12.04 | 0.1 |  |  | Skilled labour on site | 13.1944 | md | 1000 | 13194.4
| 12.05 | 0.2 |  |  | Unskilled labour on site | 26.3888 | md | 500 | 13194.4
The sand is clean and the cement is fresh, the thickness of plastering is 1.5 cm | [8 empty] | 0
A13 | 13 |  |  |  | Stone Pitching | 80 | m3 | 1000 | 80000
| 13.01 | 1 |  |  | Stone Pitching at spring area: River and boulder stone with transportation and pitching without cement and sand | 80 | m3 | 750 | 60000
| 13.02 | 0.5 |  |  | Unskilled labour on site | 40 | m3 | 500 | 20000
stone will used for protection of water from contimenation
A14 | 14 |  |  |  | GI Pipe and Fittings for river crossing | 1 | LS | 102250 | 102250
| 14.01 |  |  |  | GI-pipe 75mm for river crossing with fittings | 115 | m | 850 | 97750
| 14.02 | 3 |  |  | Unskilled labour on site | 3 | md | 500 | 1500
| 14.03 | 3 |  |  | Skilled labour on site | 3 | md | 1000 | 3000
A15 | 15 |  |  |  | Piping and fitting work of Network | 588 | m | 182.3907 | 107245.74
| 15.01 |  |  | Herat | Pipe 63mm HDPЕ 100:Pipe 63mm OD, HDPЕ 100, РN-10, Thickness 3.8 mm & Weight 0.721kg/m | 320 | m | 260 | 83200
| 15.02 |  |  | Herat | Pipe 32mm HDPЕ 100: Pipe 32mm OD, HDPЕ 100, РN-16, Thickness 2.9 mm & Weight 0.272kg/m | 35 | m | 38.5 | 1347.5
| 15.03 |  |  | Herat | Pipe 20mm HDPЕ 100: Pipe 20mm OD, HDPЕ 100, РN-16, Thickness 1.9 mm & Weight 0.112kg/m | 233 | m | 29.7 | 6920.1
| 15.04 |  |  | Herat | Supply above PE Pipe Fittings (tee, elbow, reducer coupling ….) for running the system | 1 | lot | 13720.14 | 13720.14
| 15.05 | 0.007 |  | Local | Piping work for the network and runing the water network including skill and unskilled labor | 4.116 | md | 500 | 2058
A16 | 16 |  |  |  | GI Pipe and Fittings for Water Reservoir and valve box | 17 | Lot | 1655.8824 | 28150
| 16.01 |  |  |  | GI-pipe 2.5" Drain Pipe (ill- EL- KARACHI) | 3 | M | 500 | 1500
| 16.02 |  |  | Herat | Glass wool with 5cm thickness with good quality | 3 | m2 | 250 | 750
| 16.03 |  |  |  | GI-pipe 1.5 " over flow pipe (ill- EL- KARACHI) | 2 | m | 500 | 1000
| 16.04 |  |  |  | GI-pipe 2.5" 63mm Inlet and outlet Pipe (ill- EL- KARACHI) | 6 | m | 500 | 3000
| 16.05 |  |  |  | Gate Valve 2 1/2" Cast Iron | 2 | PCS | 6200 | 12400
| 16.06 |  |  |  | All need fittings for valve connection | 1 | PCS | 8000 | 8000
| 16.07 |  |  |  | Unskilled labour on site | 1 | md | 500 | 500
| 16.08 |  |  |  | Skilled labour on site | 1 | md | 1000 | 1000
A17 | 17 |  |  |  | Pipe and Fittings for STPs | 312.12 | Lot | 136.0695 | 42470
| 17.01 |  |  | Herat | GI pipe 3/4" for tap stands | 102 | M | 150 | 15300
| 17.02 |  |  | Herat | Glass wool with 5cm thickness with good quality | 6.12 | m2 | 250 | 1530
| 17.03 |  |  | Herat | Brass valve 3/4" (Tap) | 34 | no | 260 | 8840
| 17.04 |  |  | Herat | GI elbow 3/4 | 68 | no | 110 | 7480
| 17.05 |  |  | Herat | PE femal adapter 25 to 3/4" | 34 | no | 120 | 4080
| 17.06 |  |  | Herat | Nipple 3/4" | 34 | no | 90 | 3060
| 17.07 |  |  |  | Teflon for tap installition | 34 | no | 20 | 680
| 17.08 |  |  |  | Unskilled labour on site | 1 | md | 500 | 500
| 17.09 |  |  |  | Skilled labour on site | 1 | md | 1000 | 1000
Total cost | [8 empty] | 959861.4312
Grand Total in USD | [8 empty] | 14326.29
`

## Summary sheet (hidden)
| QIN Zonal Office |  | Province: | Badghis
| Project: PCA UNICEF |  | District: | Abkamari
| Project #:A219679 |  | Village: | Haji Abdulsamad
NO | ITEMS موضوعات | UNIT واحد | Work quantity and cost estimated برآورد احجام کاری
|  |  | QUANTITY مقدار | Unit Cost (Af) قیمت فی واحد | Total cost(Afs) قیمت مجموعی
1 | Site Preparation: to clean site from all existent materials, and cleaning the spring is a part of site preparation. | M2 | 621.4 | 20 | 12428
2 | Excavation: In ordinary soil-type three and type 4 lands, excavation will be take place for different types of structure spesification. | M3 | 329.224 | 405 | 133335.72
3 | PCC (M-150, 1:2:4): The PCC work is for plecement under the collecting stand according to the drawing considering the shuttering needs, using cement sand mortar base on given specifications. • Curing should be done for minimum 7 days. | M3 | 21.5676 | 6234.9 | 134471.8292
4 | Pointing - M400(1:3) Pointing of all the joints of stone mosanry work with sandy clay mortor of M400 specification. The pointing should be uniformed and well curing is needed as per site specification and reservoir repiaring. | M2 | 30 | 229.8 | 6894
5 | RCC- M250 (1:1:2) Crushed gravel must be used, and curing must be continued up to one month, and all site engineer advicess must be considered, it's including reinforcement and shuttering work (RCC compelet work). | M3 | 11.1628 | 15056.2835 | 168070.2815
6 | Gravelling according to the drawings and specificatioon for preparation PCC work under foundation. | M3 | 57.3811 | 850 | 48773.952
7 | Painting: The work should be get done in proper way as per the drawing and specification any input of the site engineer. | M2 | 111.384 | 250 | 27846
8 | Plaster with water proof powder best quality with all nessesary works. | M2 | 46.4 | 350 | 16240
9 | Back filling from excatated materials and soft soil | M3 | 313.98 | 67.5 | 21193.65
10 | Pipe 63mm HDPЕ 100:Pipe 63mm OD, HDPЕ 100, РN-10, Thickness 3.8 mm & Weight 0.721kg/m | M | 320 | 260 | 83886
11 | Pipe 32mm HDPЕ 100: Pipe 32mm OD, HDPЕ 100, РN-16, Thickness 2.9 mm & Weight 0.272kg/m | M | 35 | 38.5 | 2033.5
12 | Pipe 20mm HDPЕ 100: Pipe 20mm OD, HDPЕ 100, РN-16, Thickness 1.9 mm & Weight 0.112kg/m | M | 233 | 29.7 | 7606.1
13 | Supply above PE Pipe Fittings (tee, elbow, reducer coupling ….) for running the system | Lot | 1 | 13720.14 | 13720.14
14 | GI-pipe 75mm for river crossing with fittings | M | 115 | 850 | 102250
15 | GI-pipe 2.5" Drain Pipe (ill- EL- KARACHI) | M | 3 | 500 | 1750 | 28150
16 | Glass wool with 5cm thickness with good quality | m2 | 3 | 250 | 1000
17 | GI-pipe 1.5 " over flow pipe (ill- EL- KARACHI) | m | 2 | 500 | 1250
18 | GI-pipe 2.5" 63mm Inlet and outlet Pipe (ill- EL- KARACHI) | m | 6 | 500 | 3250
19 | Gate Valve 2 1/2" Cast Iron | PCS | 2 | 6200 | 12650
20 | All need fittings for valve connection | PCS | 1 | 8000 | 8250 | 42469.995
21 | GI pipe 3/4" for tap stands | M | 102 | 150 | 15514.285
22 | Glass wool with 5cm thickness with good quality | m2 | 6.12 | 250 | 1744.285
23 | Brass valve 3/4" (Tap) | no | 34 | 260 | 9054.285
24 | GI elbow 3/4 | no | 68 | 110 | 7694.285
25 | PE femal adapter 25 to 3/4" | no | 34 | 120 | 4294.285
26 | Nipple 3/4" | no | 34 | 90 | 3274.285
27 | Teflon for tap installition | no | 34 | 20 | 894.285
28 | Stone Pitching at spring area: River and boulder stone with transportation and pitching without cement and sand | m3 | 80 | 1000 | 80000
29 | Plaster with cement (1:5) all areas according to drawing | m2 | 131.944 | 231.1 | 30492.2584
Total Cost |  |  |  |  | 959861.4262
14326.2899
This BoQ contains required in the Offer documents and shall be signed by a duly authorized person. Any addition, deletion or alteration in the BoQ may result in rejection of the Offer.Please have a Site visit before submit your offer and also attache the site visit picture with your bid documents | [6 empty] | #REF!
The works actually executed shall be measured, contractor shall visit the site of the works and obtain all information that may be necessary for completing their offer as under the provision of this contract no claim for additional work is accepted once the contract is signed.
Mobilization, Demobilization, Access road to construction site or other temporary works required for the execution of the items listed above, plus site restoration will be the responsibility of the contractor. Hence all the unit prices above are assumed to cover all activities associated with the works mentioned, and the total contract cost quoted is all inclusive to complete the total works.

## BoQ
MDM Rehabilitation of Health Facilities (HF) Program |  |  |  |  | Exchange rate
BoQ_Rehabilitation of Health Sub Canter for Qala-e-Fath Village-Dalaram District-Nimroz Province
S/NO | Description | Unit واحد | Quantity مقدار | Cost/Unit (AFN) قیمت فی واحد | Total Cost (AFN) قیمت مجموعی
BoQ-Need Based on Rehabilitation (Minor/specific Rehabilitation)
1 | Mobilization - Compensation in full for the cost for transport of equipment, materials and personnel on the project site | Ls | 1
2 | Boulder under for side walk, according to drawing, the unite cost includes all relevant costs i.e. materials (skill and unskilled labour) and all required works and approved by in charge engineer. | m3 | 5
3 | PCC (M-150): The PCC work for defects in OPD room, PNC room, ANC room, Nutrition room, Vaccine room and existing corridor, according to drawing, the unite cost includes all relevant costs i.e. materials (skill and unskilled labour) and all required works and approved by in charge engineer. | m3 | 2
4 | Fixing of existing rooms and corridor metallic doors, handles, locks and hinges, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. | Ls | 1
5 | Fixing of existing rooms metallic windows, handles and hinges, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. | Ls | 1
6 | Supply and Installation of screens for existing, corridor doors and windows with prepare frame, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. | Ls | 1
7 | Supply and Installation of glass for existing rooms and corridors doors and windows, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. | m2 | 17
8 | Painting work for existing room doors, windows, corridors doors and main gate doors., the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. | Ls | 1
9 | Supply and installation of MDF for partition wall, according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. | m2 | 17
10 | Painting plastic weather sheet for internal wall and ceiling of existing building ( 100% of plastic painting). | m2 | 320
11 | Straw-Mud work for roof of existing building with thickness of (5cm), according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. | m3 | 205
12 | Hollow Block with (M-250, Mix-1:4) cement mortar for side walk, according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. | m3 | 4
13 | Provision and installation of metallic sunshade for male waiting area, including oil paint works and all required items according to the drawing. | Ls | 1
14 | Supply and Installation of electrical system accessories, fittings, wiring (stranded) 1 (1C x 2.5 mm2), conduits, best quality, (electrical wiring should not be visible according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled labour) and approved by in charge engineer. | Ls | 1
15 | Supply and installation of Celling light fixture 24W,50Hz, 230V, 50Hz, clear cover luminary, Surface mounted, water proof. According to drawing with all required activity and accessories. | Nos | 12
16 | Supply and installation of 10A, 230V, Recessed mounted, two pole lighting switch's. According Viko Company to drawing with all required activity and accessories. | Nos | 6
17 | Supply and Installation of electrical system accessories, sockets, best quality according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled labour) and approved by in charge engineer. | Nos | 16
18 | Supply and Installation of water supply accessories, fitting, PPR pipe 1-inch, elbow(45 and 90), union, equal tee, reducing tee, 5wash basin, 2faucet, 2valve 1-inch and 1valve 2-inch, best quality according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled labour) and approved by in charge engineer. | Ls | 1
19 | Supply and Installation of sewer network accessories, fitting, pipe polycab 4-inch, 2Indian wc sinks, best quality according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled labour) and approved by in charge engineer. | Ls | 1
20 | Supply and Installation of sewer network accessories, fitting, pipe polycab 2-inch , best quality according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled labour) and approved by in charge engineer. | Ls | 1
21 | Supplying, Installation, laying and fitting in place of HDPE (PN16) pipe 1-inch from water point to the water tank, best quality according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled labour) and approved by in charge engineer. | m | 110
22 | Supply and Installation of 3meter cube PVC water tank with accessories, fitting, PPR pipe, elbow, wool glass, Best quality. | Nos | 1
23 | Supply and Installation of Electrical boiler 50 litters based on the design and specification with all required activities | Nos | 1
24 | Supply and installation of fire extinguisher (6kg) with all required activities | Nos | 3
1-Sub-Total Cost - Need Based on Rehabilitation (Minor/specific Rehabilitation) (AFN)
BoQ for Waste Area
1 | Construction of incinerator according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled labour) and approved by in charge engineer. | Set | 1
2 | Construction of general pit, waste pit, placenta pit and absorption pit, according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled labour) and approved by in charge engineer. | Nos | 4
3 | Supply and Installation fence surrounding of waste are with all required activities. | m | 16
4 | Supply and installation of Galvanized Iron door for waste area according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled labour) and approved by in charge engineer. | Nos | 1
2-Sub-Total Cost - Waste Area (AFN)
BoQ for Electricity Solar Panel System (3.5)kw with (5) kw Backup
1 | Supply and installation of high quality, lithium battery Pack 306AH, 5kw, Voltage 51.2v, Cycle life:6000 cycle, Growatt Brand or equivalent, completing of works with all its included details. | Nos | 1
2 | Supply and installation high quality, Monocrystalline Solar Panel Half cut double glass Grade A, 600Wp, 46.82V DA SOLAR or equivalent it should be test and confirmed by a standard laboratory completing of work with all its included details. | Nos | 6
3 | Supply and installation of high-quality,3phase Growatt hybrid inverter, 3.5kw,24VDC and weight of 20kg or its equivalent, completing of work with all its included details. | Nos | 1
4 | supply and Installation of high quality steel box 100x100x3mm structure as per drawing details / structure, completing of works with all its included details. | Nos | 1
5 | Supply and Installation cable (2*6)mm2 from solar panel to inverter | m | 30
6 | Supply and Installation cable (2*16)mm2 from inverter to battery. | m | 3
7 | Supply and installation of(1x6 mm2) single strand Annealed high conductivity copper conductor, FRLS PVC insulated 1100 V rating flexible wires for D.C side in PVC conduit. And each solar panel should be grounding. | m | 40
8 | Supply and installation of high quality 100 AMP 3phase,Manual Changeover ,completing of works with all its included details. | Nos | 1
9 | Supply and installation of high quality 20A/1000V,DC CIRCUIT BREAKER and DC SPD ,completing of works with all its included details. | Nos | 2
10 | Supply and installation of high quality 250 AMP,DC CIRCUIT BREAKER ,completing of works with all its included details. | Nos | 1
11 | Supply and installation of high quality 32 AMP,DC ISOLATROR ,completing of works with all its included details. | Nos | 2
12 | Supply and installation of high quality 63 AMP,AC ISOLATROR and AC SPD ,completing of works with all its included details. | Nos | 1
13 | Supply and installation of high quality 32 AMP,3 phase AC CIRCUIT BREAKER ,completing of works with all its included details. | Nos | 1
14 | Air condition system: Supply and installation of approved type Air condition system Cooling & Heat Pump type 9000 BTUH - 220 V-1ph-50HZ , brand: Samsung/Daikin/Carrier, complete with all necessary accessories to make it functional, For more detail & information (See Mechanical drawings Sheet# M01-M02-M03). | Set | 1
3-Sub-Total Cost - Electricity Solar Panel System (6)kw with (20) kw Backup (AFN)
BoQ for 12m3 Concrete Block Septic Tank
1 | Excavation of foundation for septic tank as per the design drawing, technical specification and with satisfaction of MDM engineer. | m3 | 23.4
2 | Back filling with soil and excavated material Ensure all construction/ foundations, pipelines is inspected and approved before backfilling begins. Remove any standing water, debris, or loose material from the excavated area. | m3 | 0.5
3 | Boulder under PCC with proper levelling and compaction from good quality and approved source of material, according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled labour) and approved by in charge engineer. | m3 | 0.53
4 | PCC (M-150): The PCC work under the foundation of septic tank according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. - Curing should be done for minimum 7 days. | m3 | 0.798
5 | Hollow Concrete Blocks (300x200x150)mm masonry wall of septic tank (thickness 30cm) with (M-250, Mix-1:4) cement mortar, according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. | m3 | 6.72
6 | Supply and Installation of roof with T-beam (12x15x5)cm and Ceiling Hollow Concrete Blocks (600x150x200)cm, according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. | m2 | 7.04
7 | Plaster work with cement-sand (Mix-1:3) for internal wall. | m2 | 20
8 | PCC work for top of septic tank (Mix-1:5), with thickness of (5cm), according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. | m3 | 0.46
9 | Supply and Placing plastic sheeting, minimum thickness (0.12)mm, as dump proof course over the top of septic tank, according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. | m2 | 9.36
10 | Supply and Installation of vitalization PVC pipe 2-inch with high of (150)cm, according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. | m | 2.5
11 | Supply and Installation of steel plate cover size ( 65x20x0.5)cm, according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. | Nos | 1
4-Sub-Total Cost - 12m3 Concrete Block Septic Tank (AFN)
BoQ for Toilets
1 | Excavation of foundation for toilers as per the design or site engineer instruction in term of wide, deep, length | m3 | 1
2 | Back filling with soil and excavated material Ensure all construction/ foundations, pipelines is inspected and approved before backfilling begins. Remove any standing water, debris, or loose material from the excavated area. | m3 | 0.45
3 | PCC (M-150): The PCC work under the foundation of toilets according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. - Curing should be done for minimum 7 days. - potable water free from impurities and within standard PH range. - Cement, OPC grade 43 high performance. Fresh product, fine and soft in side the back. | m3 | 0.2
4 | Hollow Concrete Blocks (300x200x150)mm masonry wall of toilets (thickness 30cm) with (M-250, Mix-1:4) cement mortar, according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. - Curing should be done for minimum 7 days. - potable water free from impurities and within standard PH range. - Cement, OPC grade 43 high performance. Fresh product, fine and soft in side the back | m3 | 4
5 | Supply and Installation of roof with T-beam (12x15x5)cm and Ceiling Hollow Concrete Blocks (600x150x200)cm, according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. - Curing should be done for minimum 7 days. - potable water free from impurities and within standard PH range. - Cement, OPC grade 43 high performance. Fresh product, fine and soft in side the back | m2 | 3
6 | Plaster work with cement-sand (Mix-1:3) for internal and external walls of toilets. - Clean Sand without dust, organic materials, washed. construction sand, size between 1 to 3mm. | m2 | 40
7 | Painting plastic weather sheet foe internal and external wall of toilets ( 100% of plastic painting). | m2 | 40
8 | PCC work for roof of toilets (Mix-1:5), with thickness of (5cm), according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. | m3 | 0.15
9 | Supply and Placing plastic sheeting, minimum thickness (0.12)mm, as dump proof course over the top of septic tank, according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. | m2 | 3
10 | Supply and Installation of metallic gutter, section (12x10)cm - gauge 18, 0.5m length and approved by in charge engineer. | m | 0.5
11 | Supply and Installation of door, size (0.8x2)m, with metallic frame profile (30x50)mm - gauge 18, iron sheet 1.5mm, 4 mm glass, best quality, according to the drawings. clean, with one coat of anti-rust paint and one coat of final paint, with handles, hinges, high quality lock, all related works and approved by in charge engineer. | m2 | 1.6
12 | Supply and Installation of window, size (0.3x0.3)m, with metallic frame profile (30x50)mm - gauge 18, iron sheet 1.5mm, 4 mm glass, best quality, according to the drawings. clean, with one coat of anti-rust paint and one coat of final paint, with handles, hinges, high quality lock, all related works and approved by in charge engineer. | m2 | 0.1
13 | Project sign board | Nos | 1
5-Sub-Total Cost - Toilets (AFN)
BoQ for Midwife Living Area
1 | Excavation of foundation as per the design or site engineer instruction in term of wide, deep, length. | m3 | 11
2 | Soil back filling with compaction. | m3 | 6
3 | Boulder under PCC for floor, according to drawing, the unite cost includes all relevant costs i.e. materials (skill and unskilled labour) and all required works and approved by in charge engineer. | m3 | 2.5
4 | PCC (M-150): The PCC work for floor and under the wall. according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer.. | m3 | 1.8
5 | Hollow Concrete Blocks (300x200x150)mm masonry wall (thickness 30cm) with (M-250, Mix-1:4) cement mortar, according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. - Curing should be done for minimum 7 days. | m3 | 27
6 | Supply and Installation of pre cost-beam (12x15x5)cm for doors and window lintels , according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. - Curing should be done for minimum 7 days. - potable water free from impurities and within standard PH range. - Cement, OPC grade 43 high performance. Fresh product, fine and soft in side the back | m | 18
7 | Supply and Installation of roof with T-beam (12x15x5)cm and Ceiling Hollow Concrete Blocks (600x150x200)cm, according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. | m2 | 32
8 | Supply and Placing plastic sheeting, minimum thickness (0.12)mm, as dump proof course over the top of septic tank, according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. | m2 | 23
9 | Straw-Mud work for roof of existing building with thickness of (5cm), according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. | m2 | 25
10 | PCC (M-150): The PCC work for roof. according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer.. | m3 | 3.2
11 | Gutters work (vertical from GI sheet 24 gage 10x15cm ) complete with cup. | m | 1
12 | Plaster work with cement-sand (Mix-1:3) for internal, ceiling and external walls, according to drawing, the unite cost includes its price and all relevant costs i.e. materials (skill and unskilled lobar) and approved by in charge engineer. | m2 | 165
13 | Painting plastic weather sheet foe internal and external wall of toilets ( 100% of plastic painting). | m2 | 165
14 | Provision and installation of metallic door and windows including oil paint, screen works and all required items according to the drawing. | m2 | 10.6
15 | Supply and installation of 1X24W, Door light fixtures, 230V, 50Hz, clear cover luminary, Surface mounted, water proof. According to drawing with all required activity and accessories | Nos | 5
16 | Supply and installation of 10A, 230V, Recessed mounted, two way lighting switch's. According to drawing with all required activity and accessories | Nos | 2
17 | Supply and installation of 10A, 230V, Recessed mounted, one way lighting switch's. According to drawing with all required activity and accessories | Nos | 1
18 | Supply and installation of 16A, 230V, Recessed mounted waterproof two pin sockets. According to drawing with all required activity and accessories | Nos | 3
19 | supply & installation of Stainless Steel Muslim Shower Complete Set. | set | 1
20 | supply & installation of Hand Wash Basin Complete Set. (See the Plumbing and Architectural drawings). | set | 1
6-Sub-Total Cost - Midwife Living Area (AFN)
GRAND TOTAL (AFN)

## Unit cost (hidden)
Unit Cost
No. | Item | Unit | Unit cost- Af
1 | GI-pipe 90mm for road crossing (ill- EL- KARACHI)
2 | Gate Valve 140mm Cast Iron
3 | GI-Nipple 140mm
4 | GI Union 140mm
5 | PE adapter 140mm
6 | GI-pipe 140mm (ill- EL- KARACHI)
7 | Gate Valve 75mm Cast Iron
8 | GI-Nipple 75mm
9 | GI Union 75mm
10 | PE adapter 75mm
11 | GI-pipe 75mm (ill- EL- KARACHI)
12 | Gate Valve 63mm Cast Iron
13 | GI-Nipple 63mm
14 | GI Union 63mm
15 | PE adapter 63mm
16 | GI-pipe 63mm (ill- EL- KARACHI)
17 | Gate Valve 50mm Cast Iron
18 | GI-Nipple 50mm
19 | GI Union 50mm
20 | PE adapter 50mm
21 | GI-pipe 50mm (ill- EL- KARACHI)
22 | Pipe 140mm HDPЕ 100:Pipe 140mm OD, HDPЕ 100, РN-10, Thickness 8.3 mm & Weight 3.46kg/m
23 | Pipe 110mm HDPЕ 100: Pipe 110mm OD, HDPЕ 100, РN-10, Thickness 6.6 mm & Weight 2.17kg/m
24 | Pipe 75mm HDPЕ 100:Pipe 75mm OD, HDPЕ 100, РN-10, Thickness4.5 mm & Weight 1.02kg/m
25 | Pipe 63mm HDPЕ 100:Pipe 63mm OD, HDPЕ 100, РN-10, Thickness 3.8 mm & Weight 0.721kg/m
26 | Pipe 40mm HDPЕ 100: Pipe 40mm OD, HDPЕ 100, РN-10, Thickness 2.4 mm & Weight 0.295kg/m
27 | Pipe 32mm HDPЕ 100: Pipe 32mm OD, HDPЕ 100, РN-16, Thickness 2.9 mm & Weight 0.272kg/m
28 | Pipe 25mm HDPЕ 100: Pipe 25mm OD, HDPЕ 100, РN-16, Thickness 2.3 mm & Weight 0.171kg/m
29 | Pipe 20mm HDPЕ 100: Pipe 20mm OD, HDPЕ 100, РN-16, Thickness 1.9 mm & Weight 0.112kg/m
30 | Pipe Fittings
31 | Unskilled labor on site
32 | Gravel Packing Back of Filter, 50m
33 | Pump Test
34 | cover box for well
35 | Metallic Sign Board
36 | Meter 1/2 inch Irani Talaey
37 | Well Drilling 16" dia
38 | PVC Casing Pipe 10" dia Class C
39 | PVC Filter Pipe 10" dia Class C
40 | Gravel Packing Back of Filter, 50m
41 | Backfilling of Casing Pipe with Clay, 50
42 | Pump Test and Compresor test
43 | cover box for well
44 | Metallic Sign Board
45 | Steel bar 8 mm
46 | Steel bar 10 mm
47 | Steel bar 12mm
48 | Steel bar 14 mm
49 | Steel bar 16 mm
50 | wire 1 mm
51 | Glass wool insulation (10cm thick) | Roll
52 | 3" Submersible PEDROLLO 6SR36/8 10HP 5.5Kw 400V ; 60 m3/hr at head 390m Pedrolla Made in Italy with min 2 years warranty
53 | Wire 4*6mm2 for submerssible pump
54 | Solar Pump Controler /Inverter 7.5 KW - prefered brands are Envision, Grundfos, Hober, Hober/Danfoss, JNTech, Lorentz, Shakti, Solartech, Vacon/Tommatech/Hober, Veichi, Wilo/Danfoss
55 | Solar panels: 270 Watt, TOMMATECH , LORENTZ, GRUNDFOS, POLYCRYSTALLINE Model Made in Germany with name and seriel number under the glass layer of solar panels. all solar panels specification including serial numbers must be confirmed by the companies which produce solar panels officially. Specifications: Nominal Operating Cell Temp: (-40⁰C)-(+85⁰C) Peak power (P max): 270Watt Module Efficiency: 16.47% Maximum Power Voltage: 31V Maximum Power current: 8.71A Open Circuit Voltage: 38.0V Short Circuit Current: 9.21A Cells per module: 60(6*10) Panel Dimension: 1648*995*35mm Max.Wind/Snow Load: 2400/5400Pa Weight: 18kg Performance to 10 years (min 90% power output), Performance to 25years (min 80% power output), must be confirmed by producer company, Visible lable on solar panel with technical specification.
56 | electrical solar cable 2*6mm2
57 | Maintenance box for inverter Switch
58 | Plastic Rope
59 | Stand for solar panels, able to be rotated manually
60 | Well Probe Sensor complete set
61 | Electircal sensor cable 3*1 .5mm2
62 | Float switch (Mechanical device for tank water level detection)
63 | Earthing system
64 | Delivery and Installation Cost
65 | Stationary, transportation and sign board ترانسپورت لوحه پروژه قرطاسیه | Each | 45000
66 | Shuttering قالب بندی | m2 | 270
67 | Signboard and notice board | pice | 9000
68 | Cast Iron Water Meter With Flange Adoptor | No | 22000